## Slide 1: CLOUD BASED MACHINE LEARNING APPROACHES FOR LEAKAGE ASSESSMENT AND MANAGEMENT IN SMART WATER NETWORKS
  Dr. Steve Mounce,
  Ms. Catalina Pedroza,
  Dr. Tom Jackson,
  Dr. Paul Linford and
  Prof. Joby Boxall
DMU, Leicester, UK.

## Slide 2: SmartWater4Europe
SmartWater4Europe (SW4E) is a four-year FP7 demonstration project (2014-17) funded by the EU
21 participants including three water utilities, SMEs, research organisations and platform organization
The UK demo site is focusing on leak management, integrating fixed flow and pressure instrumentation, advanced (smart) metering infrastructure, novel instruments (capable of high resolution monitoring) and data analytics
Notes: 2

## Slide 3
The four demo sites will allow demonstration of solutions incorporating sensors, data processing, modelling and ICT technologies.
Thames

## Slide 4: Demo sites
TWUL Demo site
Reading
Smart Caceres
Caceres
VIP
Leeuwarden
Sunrise Demo site
Lille
12 km
Benchmarking opportunity
Working together with some of the best in the sector

## Slide 5: Thames Water Demo Site
Reading TWIST network
870 km of distribution mains
172 km of trunk mains
45 Ml/d of chlorinated potable water
Ø from 4” (100 mm) up to 32” (800 mm)
Many pipes >60 years old
89,000 customers
4 heavily instrumented DMAs inc. ~1000 AMI
Notes: 5

## Slide 6: Leakage Management
Find leaks soon after they occur / failure mechanisms before they occur
4 DMAs featuring absolute water balance
Installation of a range of technologies
Implementing/ adapting data analytics
Initial case study
Notes: 6

## Slide 7: AURA-Alert
Advanced Uncertain Reasoning Architecture (AURA) Alert utilises the power of associative memories for novelty detection
  Provides means to train system on normality without complex underlying models
  Validate unknown data against stored states to see if unusual (novelties)
  Highly scalable approach – particularly for high volumes of Big Data
  Benefits from one-shot and high speed training
  Yet to be applied for WDS
Notes: 7

## Slide 8: AURA-Alert System

## Slide 9: AURA-Alert
Quantisation (binning process applied)
Notes: 9

## Slide 10: Methodology
Kernel that approximates to Euclidean distance gives good results (other kernels possible)
Then uses binary ANN based k-NN technique

## Slide 11: Case study analysis
Historical case study Jan 2013- June 2014
DMA inlet flows - AURA detectors were created per site with fixed width binning and default width parabolic kernels, trained with several weeks normal data (after pre-processing).
Notes: 11

## Slide 12: E8
70 Global Threshold, 1787 novelties were present out of 42912 states (~4%). AURA-Alert output can be seen in the ‘Match Distance’ channel
Highly novel flow corresponds to significant periods of zero (sensor failure) and a large abnormal increase 23/8-25/8/2013 on the flow (top) channel.
Notes: 12

## Slide 13: E14 zoom
1994 novelties out of 51757 states (~3.8%).
Notes: 13

## Slide 14: E2 zoom
DMA E2 results: 1981 novelties of 51744 states
Zoom of a detected event that was correlated with customer contact and leak repair information.
Notes: 14

## Slide 15: Conclusions
A Condition Monitoring approach for Smart Networks can allow the early detection of potential faults in assets
AURA-Alert can rapidly learn and model the normal operating envelope for a system. A continuous novelty score can be utilised to enable the detection of leak, burst and other anomalous events.
AURA-Alert is being developed as an online SaaS system which automates the training data selection and use of validation data for selecting Match Strength thresholds for alert generation. It has potential for application across many data streams simultaneously.
High sample rate data allows much greater understanding to be made available by enabling algorithms to function at a level of data quantity and resolution previously impossible.
Notes: 15

## Slide 16: Further work
Online sensor data storage and availability
AURA-Alert online enhancements for WDS specific processing and settings including ‘sequence of states’ event detection
Implement work flows and services on Cloud based portal called youShare
Integration of multiple data sources: DMA meters, Burstminders, Trunkminders, Incertameters and AMR data
Validation trials and cost benefit analysis
Notes: 16

## Slide 18: Any Questions?
With Thanks To:
http://www.smartwater4europe.com
Mounce, S. R., Mounce, R. B., Jackson, T., Austin, J. and Boxall, J. B. (2014). Associative neural networks for pattern matching and novelty detection in water distribution system time series data. Journal of HydroInformatics. Vol. 16 (3), pp. 617-632.
Further details: